Item					Frequency				Reference

Inspections_________________________________________________________________

Control valves									            Chapter 13

Fire Department connections								Chapter 13

Gauges (wet and deluge systems)		Quarterly				Chapter 13

Gauges (dry and preaction systems)		Monthly/quarterly			Chapter 13

Hanger/braces/supports			Annually				5.2.3

Heat tracing					Per manufacturer’s			5.2.6

requirements

Hydraulic design information sign		Annually				5.2.5

Information signs				Annually				5.2.7, 5.2.8, 5.2.9

Internal piping condition								Chapter 14

Pipe and fittings				Annually				5.2.2

Sprinklers					Annually				5.2.1

Sprinklers (spare)				Annually				5.2.1.4

Supervisory signal devices (except		Quarterly				5.2.4

valve supervisory switches)

System valves										Chapter 13

Valve supervisory signal devices		Quarterly				5.2.4

Waterflow alarm devices			Quarterly				5.2.4

Tests______________________________________________________________________

Antifreeze solution				Annually				5.3.3

Control valves									            Chapter 13

Gauges					            5 years				            Chapter 13

Main drain										Chapter 13

Sprinklers					At 50 years and every 10 years	5.3.1.1.1,

thereafter			5.3.1.1.1.1, 5.3.1.1.1.2

Sprinklers					At 75 years and every 5 years	5.3.1.1.1.5

thereafter

Sprinklers (dry)				10 years and every 10 years		5.3.1.1.1.6

thereafter

Sprinklers (extra high or greater		5 years				5.3.1.1.1.4

temperature solder type)

Sprinklers (fast-response)			At 20 years and every 10 years	5.3.1.1.1.3

thereafter

Sprinklers (harsh environments)		5 years				5.3.1.1.2

Supervisory signal devices (except							Chapter 13

valve supervisory switches)

System valves										Chapter 13

Valve supervisory signal devices							Chapter 13

Waterflow alarm devices			Quarterly				5.3.2.1

(Mechanical)

Waterflow alarm devices (vane and		Semiannually				5.3.2.2.

pressure switch type)

Maintenance

Low-point drains (dry pipe and							Chapter 13

preaction systems)

Sprinklers and automatic spray		Annually				5.4.1.7

nozzles protecting commercial

cooking equipment and ventilation

systems

Valves (all types)									Chapter 13

Investigation

Obstruction										Chapter 14